## BOQ_AS PER DSR
NAME OF WORK : ENTREPRENEURSHIP DEVELOPMENT INSTITUTE
DOCUMENT : BILL OF QUANTITY FOR CIVIL CONSTRUCTION WORKS FOR FIRE UNDER GROUND WATER TANK
S/N. | DSR NO | ITEM OF WORKS | QUANTITY | UNIT | RATE | AMOUNT [RS.]
Schedule - A1 - Civil Works.
1 | 2.8.1 Page No: 92 | Earth work in excavation by mechanical means (Hydraulic excavator) / manual means in foundation trenches or drains (not exceeding 1.5 m in width or 10 sqm on plan), including dressing of sides and ramming of bottoms, lift upto 1.5 m, including getting out the excavated soil and disposal of surplus excavated soil as directed, within a lead of 50 m. a. All Kind of Soils | 133 | Cu.m
2 | 2.9 Page No: 93 | Excavation work by mechanical means (Hydraulic excavator)/ manual means in foundation trenches or drains (not exceeding 1.5m in width or 10 sqm on plan), including dressing of sides and ramming of bottoms, lift upto 1.5 m, including getting out the excavated soil and disposal of surplus excavated soils as directed, within a lead of 50 m.
2a | a. | Ordinary rock | Rate only | Cu.m
2b | b. | Hard rock (requiring blasting) | Rate only | Cu.m
2c | c. | Hard rock (blasting prohibited) | Rate only | Cu.m
3 | 2.26 Page No: 95 | Extra for every additional lift of 1.5 m or part thereof in excavation / banking excavated or stacked materials. [From 1.5m Depth to 5.0m Depth]
3a | a. | All kinds of soil | 172 | Cu.m
3b | b. | Ordinary rock or Hard Rock | Rate only | Cu.m
4 | 16.78 Page No: 284 | Construction of granular sub-base by providing close graded Material conforming to specifications, mixing in a mechanical mix plant at OMC, carriage of mixed material by tippers to work site, for all leads & lifts, spreading in uniform layers of specified thickness with motor grader on prepared surface and compacting with vibratory power roller to achieve the desired density, complete as per specifications and directions of Engineer-in-Charge. With material conforming to Grade-I (size range 75 mm to 0.075 mm) having CBR Value-30 | 2 | Cu.m
5 | 2.27 Page No: 95 | Supplying and filling in plinth with sand under floors, including watering, ramming, consolidating and dressing complete | Rate only | Cu.m
6 | 2.28 Page No: 96 | Surface dressing of the ground including removing vegetation and inequalities not exceeding 15 cm deep and disposal of rubbish, lead up to 50 m and lift up to 1.5 m. A. All kinds of soil | 100 | Sq.m
7 | 2.25 Page No: 95 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. | 116 | Cu.m
8 | 2.25 a Page No: 95 | Excavating, supplying and filling of local earth (including royalty) by mechanical transport upto a lead of 5km also including ramming and watering of the earth in layers not exceeding 20 cm in trenches, plinth, sides of foundation etc. complete | Rate only | Cu.m
7 | 2.34 Page No: 96 | Supplying chemical emulsion in sealed containers including delivery as specified. Chlorpyriphos/ Lindane emulsifiable concentrate of 20% | 218 | Liter
8 | 2.35.2 Page No:96 | Diluting and injecting chemical emulsion for POST-CONSTRUCTIONAL anti-termite treatment (excluding the cost of chemical emulsion) : Along the external wall below concrete or masonry apron using chemical emulsion @ 2.25 litres per linear metre including drilling and plugging holes etc.: With Chlorpyriphos/ Lindane E.C. 20% with 1% concentration | 39 | Meter
9 | 2.35.3 Page No:97 | Treatment of soil under existing floors using chemical emulsion @ one litre per hole, 300 mm apart including drilling 12 mm diameter holes and plugging with cement mortar 1 :2 (1 cement : 2 Coarse sand) to match the existing floor: With Chlorpyriphos/Lindane E.C. 20% with 1% concentration | 100 | Sq.m
10 | 4.1.5 Page No:107 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level 1:3:6 (1 Cement : 3 coarse sand (zone-III) : 6 graded stone aggregate 20 mm nominal size | 16 | Cu.m
11 | 4.1.8 Page No:107 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level 1:4:8 (1 Cement : 4 coarse sand (zone-III) : 8 graded stone aggregate 20 mm nominal size | Rate only | Cu.m
11 | 5.33 Page No:129 | Providing and laying in position ready mixed or site batched design mix cement concrete for reinforced cement concrete work; using coarse aggregate and fine aggregate derived from natural sources, Portland Pozzolana / Ordinary Portland /Portland Slag cement, admixtures in recommended proportions as per IS: 9103 to accelerate / retard setting of concrete, to improve durability and workability without impairing strength; including pumping of concrete to site of laying, curing, carriage for all leads; but excluding the cost of centering, shuttering, finishing and reinforcement as per direction of the engineer-in-charge; for the following grades of concrete. Note: Extra cement up to 10% of the minimum specified cement content in design mix shall be payable separately. In case the cement content in design mix is more than 110% of the specified minimum cement content, the contractor shall have discretion to either re-design the mix or bear the cost of extra cement.
12 | 5.33.1 Page No:129 | All works up to Plinth level.
12A | 5.33.1.1 Page No:129 | Concrete of M25 grade with minimum cement content of 330 kg /cum | 65 | Cu.m
12B | 5.33.1.2 Page No:129 | Concrete of M30 grade with minimum cement content of 350 kg /cum | Rate only | Cu.m
13 | 5.33.2 Page No:129 | All works above plinth level upto floor V level
13A | 5.33.2.1 Page No:129 | Concrete of M25 grade with minimum cement content of 330 kg /cum | 7.2 | Cu.m
13B | 5.33.2.2 Page No:129 | Concrete of M30 grade with minimum cement content of 350 kg /cum | Rate only | Cu.m
13C | 5.33.2.3 Page No:129 | Concrete of M35 grade with minimum cement content of 370 kg /cum | Rate only | Cu.m
14 | 5.22 Page No: 127 5.22.6 | Steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete upto plinth level. Thermo-Mechanically Treated bars of grade Fe-500D or more | 6290 | Kg.
15 | 5.22a Page No:127 5.22A.6 | Steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete above plinth level. Thermo-Mechanically Treated bars of grade Fe-500D or more. | 1025 | Kg.
16 | 5.9 Page : 96 | Centering and shuttering including strutting, propping etc. and removal of form for :
17 | 5.9.1 Page : 123 | Foundations, footings, bases of columns, etc. for mass concrete | 12 | Sq.m
18 | 5.9.2 Page : 123 | Walls (any thickness) including attached pilasters, butteresses, plinth and string courses etc. | 210 | Sq.m
19 | 5.9.3 Page : 123 | Suspended floors, roofs, landings, balconies and access platform | Rate only | Sq.m
20 | 5.9.5 Page : 123 | Lintels, beams, plinth beams, girders, bressumers and cantilevers | Rate only | Sq.m
21 | 5.9.6 Page : 123 | Columns, Pillars, Piers, Abutments, Posts and Struts | 16 | Sq.m
22 | 5.9.7 Page : 123 | Stairs, (excluding landings) except spiral-staircases | Rate only | Sq.m
23 | 5.9.20 Page : 124 | Suspended floors, roofs, landings, balconies and access platform with water proof ply 12 mm thick | 80 | Sq.m
24 | 5.9.21 Page : 124 | Lintels, beams, plinth beams, girders, bressumers and cantilevers with water proof ply 12 mm thick | 11 | Sq.m
25 | 5.11.1 Page : 124 | Extra for additional height in centering, shuttering where ever required with adequate bracing, propping etc., including cost of de-shuttering and decentering at all levels, over a height of 3.5 m, for every additional height of 1 metre or part thereof (Plan area to be measured). Suspended floors, roofs, landing, beams and balconies (Plan area to be measured) | Rate only | Sq.m
26 | NON DSR | Surface Preparation [Internal and External / External and Floor Treatment] : All surfaces to be waterproofed should be made sound, clean and dry. Concrete surfaces should have a light steel-trowel followed by a fine hair-broom or equivalent finish, which is dry and free of dust, oil and other contaminants. Sharp projection, moss and lichen must be removed physically followed by treatment with fungicidal wash to kill any spores and inhibit further growth. Grouting periphery of spout pipes , construction joints and honey comb areas with appropriate materials, proper preparation of the concrete surface by mechanical means/hydro blasting to ensure a good bond between the topping and the substrate.
27 | A. | Treatment of Bore Packing / In Let pipes/Out let Pipes Use Mapei thixo Tropic Grout and Mape Proof Swell | Rate only | Per Hole
28 | B. | Application of Mapeband Tape on Corner joint (Only Horizontal & Vertical Joints) | 160 | Rmt.
29 | c. | Providing and Application of waterproofing coating on the properly treated concrete surface – Planiseal 288 Plus Planiseal 288 Plus must be applied in at least two coats by brush or with a roller within 60 minutes of it being mixed, to give a final thickness of at least 2 mm. Planiseal 288 Plus on horizontal surfaces by flat-bladed trowel. After applying Planiseal 288 Plus , wait at least 4 Days for Pond Testing. Work shall be carried out as per engineer in charge and manufacter specification | 197 | Sq.m
30 | 22.7 .1 Page : 471 | Providing and laying integral cement based water proofing treatment including preparation of surface as required for treatment of roofs, balconies, terraces etc consisting of following operations: a). Applying a slurry coat of neat cement using 2.75 kg/sqm of cement admixed with water proofing compound conforming to IS. 2645 and approved by Engineer-in-charge over the RCC slab including adjoining walls upto 300 mm height including cleaning the surface before treatment. b). Laying brick bats with mortar using broken bricks/brick bats 25 mm to 115 mm size with 50% of cement mortar 1:5 (1 cement : 5 coarse sand) admixed with water proofing compound conforming to IS : 2645 and approved by Engineer-in-charge over 20 mm thick layer of cement mortar of mix 1:5 (1 cement :5 coarse sand ) admixed with water proofing compound conforming to IS : 2645 and approved by Engineer-in-charge to required slope and treating similarly the adjoining walls upto 300 mm height including rounding of junctions of walls and slabs c). After two days of proper curing applying a second coat of cement slurry using 2.75 kg/ sqm of cement admixed with water proofing compound conforming to IS : 2645 and approved by Engineerin-charge. d). After two days of proper curing applying a second coat of cement slurry using 2.75 kg/ sqm of cement admixed with water proofing compound conforming to IS : 2645 and approved by Engineerin-charge. e). The whole terrace so finished shall be flooded with water for a minimum period of two weeks for curing and for final test.“All above operations to be done in order and as directed and specified by the Engineer-in-Charge : With average thickness of 120 mm and minimum thickness at khurra as 65 mm. | 28 | Sq.m
31 | 6.1.1 Page : 139 | Brick work with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in foundation and plinth in: Cement Mortar 1:4 (1 cement : 4 coarse sand) | Rate only | Cu.m
32 | 6.4.1 Page : 139 | Brick work using semi-exposed (semi-exposed finish as per prevailing site quality) burnt clay building bricks having crushing strength not less 50 kg. /sq. cm. in Cement Mortar 1:6 in Superstrucutre above plinth level for GF. (B) Conventional. | 13 | Cu.m
33 | 6.12 Page : 140 | Half brick masonry with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in foundations and plinth in : : Cement mortar 1:4 (1 cement : 4 coarse sand) | Rate only | Sq.m
34 | 6.13 Page : 140 | Half brick masonry with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in in superstructure above plinth level up to floorV level. Cement mortar 1:4 (1 cement : 4 coarse sand) | Rate only | Sq.m
35 | 6.38 Page : 142 | Providing and laying autoclaved aerated cement blocks masonry with 100 mm thick AAC blocks in super structure above plinth level up to floor V level in cement mortar 1:4 (1 cement : 4 coarse sand ). The rate includes providing and placing in position 2 Nos 6 mm dia M.S. bars at every third course of masonry work | Rate only | Cu.m
36 | 6.47 Page : 143 | Providing and laying autoclaved aerated cement blocks masonry with 150mm / 230mm / 300 mm thick AAC blocks in super structure above plinth level up to floor V level with RCC band at sill level and lintel level with approved block laying polymer modified adhesive mortar all complete as per direction of Engineer-in-Charge. (The payment of RCC band and reinforcement shall be made for seperately). | Rate only | Cu.m
37 | 11.37 Page : 240 | Providing and laying Ceramic glazed floor tiles of size 300x300 mm (thickness to be specified by the manufacturer) of 1st quality conforming to IS : 15622 of approved make in colours such as White, Ivory, Grey, Fume Red Brown, laid on 20 mm thick cement mortar 1:4 (1 Cement : 4 Coarse sand), Jointing with grey cement slurry @ 3.3 kg/sqm including pointing the joints with white cement and matching pigment etc., complete. | 42 | Sq.m
38 | 8.31 Page : 162 | Providing and fixing Ist quality ceramic glazed wall tiles of size 300x300mm conforming to IS: 15622 (thickness to be specified by the manufacturer), of approved make, in all colours, shades except burgundy, bottle green, black of any size as approved by Engineer-in-Charge, in skirting, risers of steps and dados, over 12 mm thick bed of cement mortar 1:3 (1 cement : 3 coarse sand) and jointing with grey cement slurry @ 3.3kg per sqm, including pointing in white cement mixed with pigment of matching shade complete. | 113 | Sq.m
39 | 11.43 Page : 242 | Fixing glazed/ Ceramic/ Vitrified floor tiles with cement based high polymer modified quick-set tile adhesive (Water based) conforming to IS: 15477, in average 3mm thickness. | 113 | Sq.m
40 | 11.26 Page : 239 | Kota stone slab flooring having even color tone, over 25 to 30 mm (average) thick base laid over and jointed with grey cement slurry mixed with pigment to match the shade of the slab, including rubbing and polishing complete with base of cement mortar 1 : 4 (1 cement : 4 coarse sand) : 25mm Thick | 56 | Sq.m
41 | 11.27 Page : 239 | Kota stone slab flooring having even color tone, over 25 to 30 mm (average) thick in risers of steps, skirting, dado and pillars laid on 12 mm (average) thick cement mortar 1:3 (1 cement: 3 coarse sand) and jointed with grey cement slurry mixed with pigment to match the shade of the slabs, including rubbing and polishing complete. | 10 | Sq.m
42 | NON DSR | Providing & laying broken white china mosaic flooring for plain and curved surfaces, comprising of 18 mm to 25 mm. size broken pieces of glazed tiles of even colour and shade, laid over cement mortar 1:6 bedding including applying cement slurry at the rate of 2.75 kg per sq.m. , on plain or sloped surfaces. The flooring shall be tampered to bring the mortar upto the surface, including grouting the joints with white cement & rounding of the junctions and extending them upto 15cm along the parapet wall, including curing, cleaning with water and oxalic acid etc. complete for all floors / all levels / all heights and all as per specifications and direction of Engineer-in-charge. (Plan are a shall be measured & paid. Vata shall not be considered for Payment Purpose) | 28 | Sq.m
43 | 11.31 Page : 240 | Extra for pre finished nosing of Kota stone/ sand stone slab. | 17 | Rmt.
44 | 13.4 Page : 278 | Cement Plaster [in Coarse Sand] : 12mm Cement Plaster [1:4] [1: Cement and 4 ; Coarse sand] | 42 | Sq.m
45 | 13.12 Page : 279 | 18 mm cement plaster in two coats under layer 12 mm thick cement plaster 1:5 (1 cement : 5 coarse sand) finished with a top layer 6 mm thick cement plaster 1:6 (1 cement : 6 fine sand) | 42 | Sq.m
46 | 13.12 Page : 279 | 18 mm cement plaster in two coats under layer 12 mm thick cement plaster 1:5 (1 cement : 5 coarse sand) and a top layer 6 mm thick cement plaster 1:3 (1 cement : 3 coarse sand) finished rough with sponge. | Rate only | Sq.m
47 | 13.14 Page : 279 | 15 mm cement plaster 1:3 (1 cement: 3 coarse sand) finished with a floating coat of neat cement on the RCC or Brick wall | 126 | Sq.m
48 | 13.21 Page : 280 | Extra for providing and mixing water proofing material in cement plaster work in proportion recommended by the manufacturers. | 35 | per bag of 50kg cement used in the mix
48 | 13.80 Page : 286 | Providing and applying white cement based putty of average thickness 1 mm, of approved brand and manufacturer, over the plastered wall surface to prepare the surface even and smooth complete. | 42 | Sq.m
49 | 13.82.2 Page : 236 | Wall painting with premium acrylic emulsion paint of interior grade, having VOC (Volatile Organic Compound ) content less than 50 grams/ litre of approved brand and manufacture, including applying additional coats wherever required to achieve even shade and colour. Two Coats | 42 | Sq.m
50 | 13.43 Page : 282 | Applying one coat of water thinnable cement primer of approved brand and manufacture on wall surface : Water thinnable cement primer | 80 | Sq.m
51 | 13.45.1 Page : 282 | Exterior Finishing : Finishing walls with textured exterior paint of required shade. New work (Two or more coats applied @ 3.28 ltr/10 sqm) over and including priming coat of exterior primer applied @ 2.20kg/10 sqm | Rate only | Sq.m
52 | 13.46.1 Page : 282 | Exterior Finishing : Finishing walls with Premium Acrylic Smooth exterior paint with Silicone additives of required shade: New work (Two or more coats applied @ 1.43 ltr/10 sqm over and including priming coat of exterior primer applied @ 2.20 kg/10 sqm) | Rate only | Sq.m
53 | NON DSR | Providing and applying Silicone paint SILRES (R) BS 290 of Wacker -1 liter & 13 liter solvent of recommended make or approved equivalent over exposed concrete surfaces (Two coats on wet on wet applied ) etc complete as directed by the Engineer-in-charge, so as original look does not change. The contractor shall furnish a minimum 5 years guarantee on stamp paper to the employer directly.(sample to be approved) | 128 | Sq.m
54 | 10.16 Page : 226 | Steel work in built up tubular (round, square or rectangular hollow tubes etc.) trusses etc., including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer, including welding and bolted with special shaped washers etc. complete. Hot finished welded type tubes | Rate only | Kg.
55 | 21.1.1.2 Page : 460 | Providing and fixing aluminium work for doors, windows, ventilators and partitions with extruded built up standard tubular sections/ appropriate Z sections and other sections of approved make conforming to IS: 733 and IS: 1285, fixing with dash fasteners of required dia and size, including necessary filling up the gaps at junctions, i.e. at top, bottom and sides with required EPDM rubber/ neoprene gasket etc. Aluminium sections shall be smooth, rust free, straight, mitred and jointed mechanically wherever required including cleat angle, Aluminium snap beading for glazing / paneling, C.P. brass / stainless steel screws, all complete as per architectural drawings and the directions of Engineer-in-charge. (Glazing, paneling and dash fasteners to be paid for separately). Powder coated aluminium (minimum thickness of powder coating 50 micron) | 24 | Kg.
56 | 21.3.2 Page : 461 | Providing and fixing glazing in aluminium door, window, ventilator shutters and partitions etc. with EPDM rubber / neoprene gasket etc. complete as per the architectural drawings and the directions of engineer-in-charge . (Cost of aluminium snap beading shall be paid in basic item): With float glass panes of 5 mm thickness (weight not less than 12.50 kg/sqm) | 3 | Sq.m
57 | 9.20 Page : 186 | Providing and fixing ISI marked flush door shutters conforming to IS : 2202 (Part I) decorative type, core of block board construction with frame of 1st class hard wood and well matched teak 3 ply veneering with vertical grains or cross bands and face veneers on both faces of shutters. 35 mm thick including ISI marked Stainless Steel butt hinges with necessary screws | 5 | Sq.m
58 | 9.22 Page : 186 | Extra for Providing and fixing flush doors with decorative veneering instead of non decorative ISI marked flush door shutters conforming to IS: 2202 (Part I) On One Side Only | 2.5 | Sq.m
59 | 9.23 Page : 150 | Extra for providing lipping with 2nd class teak wood battens 25 mm minimum depth on all edges of flush door shutters (over all area of door shutter to be measured). | 5 | Sq.m
60 | 12.22 Page : 260 | Making khurras 45x45 cm with average minimum thickness of 5 cm cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate of 20 mm nominal size) over P.V.C. sheet 1 m x1 m x 400 micron, finished with 12 mm cement plaster 1:3 (1 cement : 3 coarse sand) and a coat of neat cement, rounding the edges and making and finishing the outlet complete. | 1 | Nos.
61 | 22.26 Page : 475 | Providing and applying of swellable type water stop tape, 19mm x 25mm thick in linear meter (expansive nature) for construction joints treatment of RCC structure such as raft slab, retaining walls, water storage tank and at the junctions of raft slab with the retaining walls etc.. After cleaning the surface, one coat of required primer for swellable water stop tape shall be applied throughout the length of the joint @3.78 litre per 240 running meter. Over the primed surface swellable type water stop tape shall be placed. The work shall be carried out all complete as per specification and the direction of the Engineer-In-Charge. The product performance shall carry guarantee for 10 years against any leakage. | 160 | Rmt.
62 | NON DSR | Providing and Fixing Cast Iron Foot Rest of Sizes [5.45"x 12"] having unit weight 4.0 Kg per No. Rate shall include fixing in position in true line, level as per details including all tools , tackles, labours and equipement for fixing of the foot rest. Rate shall include required scaffolding wherevery necessary for all height / all level / all depths etc complete. Rate shall be inclusive of Anticorrossive paint. Work shall be carried out as per direction and instruction of Engineer in charge. | 51 | Nos.
Total of Schedule - A1
Schedule - A2 - Fire Fighting Works
A |  | PUMP HOUSE EQUIPMENT
1 |  | Supply, Installation, Testing & Commissioning of Electrical driven Main Fire Pump that shall be capable of giving a discharge of not less than 150 per cent of the rated discharge, at a head of not less than 65 per cent of the rated head. The shut off head shall be within 120 per cent of the rated head.Pumps shall be Horizontal end suction fire pumps having cast iron casing, cast iron diffusers, bronze impellers and dynamically balanced, AISI 304/410 stainless steel shaft running in double ball bearings. Each pump shall be fitted with gland packing and shall be directly coupled on an MS fabricated common base plate to Squirrel cage A.C. induction type suitable for operation on 415 volts 3 phase 50 Hz. system. The motor shall be totally enclosed fan cooled type conforming to protection clause IP 55, IE 2 Rated. The class of insulation shall be F. The synchronous speed shall be 1500 RPM as specified. The motor shall be rated for continuous duty and shall have a horse power rating necessary to drive the pump at 150 per cent of its rated discharge with at least 65 per cent rated head. The motor shall conform to I.S.325-1978. Complete set shall be mounted on common base frame. The quoted rate shall include providing & fixing of coupling, coupling guard, RCC foundation will be done by Civil contractor (as recommended by pump manufacturer) Foundation bolts to be considered by fire vendor etc. Adequate number of Anti Vibration Mounting Pads, "RESISTOFLEX" or make as per manufacturer's recommendations. Make - Lubi, Xylem
a) |  | Pump shall be capable of delivering a capacity of 1600 LPM at a total head of 80 mtrs. | 0 | set
b) |  | Pump shall be capable of delivering a capacity of 2280 LPM at a total head of 80 mtrs. | 1 | set
2 |  | Supply, erection, testing & commissioning of Electrical motor driven Jockey pump of vertical in line type with gland packing and capable to deliver 180LPM at 80 head Jockey Pump shall have SS casing, cast iron diffusers, SS /bronze impellers and dynamically balanced, AISI 410 stainless steel shaft and pump base. Each pump shall be fitted with mechanical seals and shall be directly coupled on motor stool with AC 3 phase, 2900 RPM TEFC IE 2 motor. The quoted rate shall include providing & fixing of coupling, MS epoxy coated Base plate, RCC foundation shall be constructed by civil contactor ( as recommended by manufacturer) and Foundation bolts, etc. | 1 | set
3 |  | Supply,Installation, Testing and commissioning of Water Curtain Pump with Horizontal centrifugal pumping set capable to deliver 162 LPM at 40 MWC having cast iron casing, cast iron diffusers, bronze impellers and dynamically balanced, AISI 304/410 stainless steel shaft running in double ball bearing shaft as per IEC standards and GJL250 cast iron suction & discharge casing, connected to TEFC ventilated induction motor of 2 pole, 2900 RPM, suitable for 400/440 volts, 3 phase, 50 Hz 3 phase AC supply, Class F insulation with vibration elimination pads etc. complete with factory fitted base and frame, nuts and bolts as per instructions suitable for following duty. | RO | set
4 |  | ELECTRICAL CONTROL PANEL FOR FIRE PUMPS
a) |  | Supply Installation, assembly, connection, testing and commissioning of Panel as per Drawing, Specification, Technical Data sheet & IS.Panel shall be manufactured CPRI approved panel manufacturer with inhouse 7 tank process and painting facility. The unit rate for each item shall include Testing of panels as per specifications at manufacturer's works in presence of clients representative and/or consultant.Supply & delivery of the panels at the site.Assembly and wiring of component supplied separately.Installation of panels as per lcoation arranged by site engineer in charge including removing packing.'Shifting of panels from site store to the suitable location.(If applicable).Installation of panels as per lcoation arranged by site engineer in charge including removing packing.Earthing all components, frame etc. to a common internal earth bar.Supply & fixing all accessories and supporting structure.'Toching of body with poweder coating for demaged parts. All the nuts bolts & joints exposed to the air shall be covered with suitable anti-oxidant material or as directed by the Engineer incharge.To carry out the insulation test at site and all the readings shall be submitted in duplicate to the consultant or engineer-in-charge.To prepare submission drawing and to take approval of consultant at each stage.For panel MS angle stand required. ( Size MS angle & height of stand as per Panel Weight & size of cable termination requirement to be calculate by panel vendor, need to confirm with desing Consultant).Checking of Internal connection and wiring, operation of switches, starter, MCCB, MCB, relays, contactors etc.Supply of necessary tools, hardware, testing hardware, testing equipment etc.To prepare & submit as-built drawing and handing over document to end user.Approval from consultant required before fabrication of panel. LT SWITCHGEAR (MCCB) :- MP & TM LEGRAND – DPX3 / SCHNIEDER - CVS / SIEMENS – 3VA LT SWITCHGEAR (MCB) :- LEGRAND - DX3 / SCHNIEDER – ACTI 9 / SIEMENS - 5SL(10kA) 1. B curve MCB shall be quoted for resistive loads. 2. C cuve MCB shall be quoted for slightly inductive loads. 3. D curve MCB shall be quoted for small motroised loads, UPS, pumps etc. Refer SLD for the same. Make: L & T | 1 | set
FIRE FIGHTING PANEL as per Specification, Technical Data sheet & make list.Refer Single line diadram-. (TYPE- 2 CO-ORDITAION REQUIRED FOR CONTACTOR & I/C AND O/G MCCB & STARTER.) Change over switch : 400 A FP Automatic change over switch With RYB indication lamp. Incoming : 200A,4P,35 KA,MCCB WITH THERMAL MAGE. BASED RELEASE (O/L,S/C,E/F PROTE.) with CT and MFM & ON,OFF,TRIP & RYB indication lamp Busbar : 250 A, 415V, 4P,35kA, 50Hz,AL. BUSBAR Outgoing :(A)2 NOS. 160 A FP 35 KA,MCCB WITH THERMAL MAGE. BASED RELEASE (O/L,S/C,E/F PROTE.) with CT and MFM & ON,OFF,TRIP indication lamp (B)1 NOS. 40 A FP MCB 10KA (D-Curve), 1 NOS. 32 A DP MCB 10KA (D-Curve) with ON OFF indication & DG ON, OFF indication lamp and SPD (8/350 μs current wave,125 ka, mcov:-1.2 kv) & other required accesories. (C) Fully Automatic Star-Delta Starter for above motors suitable for upto 75 HP with Electronic Overload,single phasing protection and reverse phase protection, Auto/Manual/Remote/Off Selector Switch, Push Button for Manual Start & Stop,Alarm with reset push button which will automatically reset for the next cycle, LED Type indication for ON/OFF/ TRIP status and digital motor protection relay and hoot ,star delta timer ,A-meter with selector switch with ct and provision for pressure switch control. & other required accesories (refer single line diagram). -1 nos. (D) Fully Automatic Star-Delta Starter for above motors suitable for upto 10 HP with Electronic Overload,single phasing protection and reverse phase protection, Auto/Manual/Remote/Off Selector Switch, Push Button for Manual Start & Stop,Alarm with reset push button which will automatically reset for the next cycle, LED Type indication for ON/OFF/ TRIP status and digital motor protection relay and hoot ,star delta timer ,A-meter with selector switch with ct and provision for pressure switch control. & other required accesories (refer single line diagram). -1 nos. (E) Control panel for diesel engine driven pump Auto/Manual/Remote/Off Selector Switch, Push Button for Manual Start & Stop,Alarm with reset push button which will automatically reset for the next cycle, LED Type indication for ON/OFF/ ACON/DCON/DG SET TO START FAIL and hooter with engine cranking relay and battery charging with auxilary relay. & other required accesories (refer single line diagram). -1 nos.
5 |  | Supply, erection, testing & commissioning of Pressure switches of diaphram operated SPDT type IP 36 suitable range (20 kg/cm² to 5 kg/cm²) for pump sets with Ball valves, Fittings like unions / collars / reducers etc. Make : INFOSS | 2 | nos
6 |  | Supply, erection, testing & commissioning of Pressure gauges of suitable range (0 kg/cm² to 30 kg/cm²) for pump sets with Ball valves, SS /Cu siphon tube, Fittings like unions / collars / reducers etc. Make: H Guru | 2 | nos
7 |  | SITC of Emergency ON-OFF Push Button Stations in Fire Red Colour MS power coated enclosure IP 54 with in-built indicating lamp, auto, manual switch for remote operation. | 1 | set
8 |  | Supplying, installing, testing and commissioning of ERW G.I. Pipes confirming to IS 3589,6mm thick, with painting, suitable type of supports, anchor fasteners, bolts nuts (Galvanized), clamps, "U" bolts, fittings such as Reducers,Tees, elbows, flanges. Including cutting, Welding, fixing in / on walls, ceiling by using suitable supports etc. The quoted rate shall also include for chasing / chipping walls, floor and making them good with filler material and finished in cement morter etc. complete.
a) |  | 250mm nominal dia | RO | m
b) |  | 200mm nominal dia | 5 | m
9 |  | Supplying, installing, testing and commissioning of ERW G.I. Pipes confirming to IS 1239 Part - I Heavy grade with painting, suitable type of GI pre-formed supports, anchor fasteners, bolts nuts (Galvanised), Rubber Sleeved clamps, "Rubber Sleeved U" bolts, fittings such as reducers,tees, elbows, flanges including cutting,welding, fixing in / on walls, ceiling by using suitable supports etc, as per drawings. The quoted rate shall also include for chasing / chipping walls and making them good with filler material and finished in cement morter etc. complete.
a) |  | 150mm nominal dia | 5 | m
b) |  | 100mm nominal dia | 130 | m
c) |  | 80mm nominal dia | RO | m
d) |  | 65mm nominal dia | RO | m
e) |  | 50mm nominal dia | RO | m
f) |  | 25mm nominal dia | RO | m
10 |  | Providing protection to under ground pipes and fittings by applying protective primer thereafter wrapping with Pypkote or equivalent material of 4mm thick & 110 mm width protection coating as per IS:10221 by thermo fusion process. Overlap shall be maintained at 15mm the application process shall be strictly according to manufacturer's specification. | 130 | m
11 |  | Excavation of soft soil including backfilling & compacting. | 130 | M³
12 |  | Supplying, Installing, testing and commissioning CI Butterfly valves (PN 16) as per BS 5155 with SG Iron disc, slim seal with required flanges, nuts, bolts etc. complete.
a) |  | 200mm nominal dia (Lever operated) | 2 | nos
b) |  | 150mm nominal dia (Lever operated) | 2 | nos
c) |  | 100mm nominal dia (Lever operated) |  | nos
d) |  | 80mm nominal dia (Lever operated) |  | nos
e) |  | 65mm nominal dia (Lever operated) |  | nos
13 |  | Supplying, installing, testing and commissioning of Forged Brass chrome finished Ball Valves (PN 16) with fittings of screwed end type.
a) |  | 25 mm dia | 1 | nos
b) |  | 50 mm dia |  | nos
14 |  | Supplying, installing and commissioning C.I.flanged "Y" type Strainer with SS mesh,suitable flanges, nuts, bolts, gaskets etc. complete.
a) |  | 200mm dia. | 1 | nos
b) |  | 150mm dia. |  | nos
c) |  | 100mm dia. |  | nos
d) |  | 80mm dia. |  | nos
15 |  | Supplying, installing, testing and commissioning of C.I. Non-return valves as per IS:5312( PN 16) dual plate type with required flanges, nuts, bolts and gaskets etc. complete.
a) |  | 200 mm nominal dia |  | nos
b) |  | 150 mm nominal dia | 1 | nos
c) |  | 100 mm nominal dia |  | nos
d) |  | 80 mm nominal dia |  | nos
d) |  | 65 mm nominal dia | 1 | nos
16 |  | Supplying, installing, testing and commissioning of Rubber Flexible Bellows ( Make: Dunlop/Resistoflex) suitable for 16 bar pressure with required GI flanges, nuts, bolts and gaskets etc. complete.
a) |  | 200mm dia. | 2 | nos
b) |  | 150 mm nominal dia | 2 | nos
c) |  | 80 mm nominal dia |  | nos
d) |  | 65 mm nominal dia | 1 | nos
Total of Schedule - A2
Schedule - A3 -Plumbing Works
1.1 |  | HYDROPNEUMATIC PUMPSETS for Supplying Boosted Water
Variable Speed VFD Driven in-line, vertical multistage, centrifugal clear water pumps, speed upto 2900 rpm, with CI / SS Suction & Discharge chamber and SS casing (body), S.S 304 impeller and SS-304/410 shaft, C.I. Base with electro coating , connected to a TEFC motor (with mechanical seal) suitable for 380 / 440 volts, 3 phase 50 cycles A.C. supply, SKID mounted Electrical Control Panel , GI Suction & Discharge headers with valves and accessories, Hydro booster pressure vessel rated for 20 bar pressure of approx. 100 liters capacity on common CI/MS epoxy painted skid. Pumpsets to be fixed on RCC/PCC foundation with foundation bolts /vibration eleminating pads as required. ( Anti Vibration /foundation Pads, base frame shall be supplied by vendor)
Skid mounted Electrical Starter panel IP 42 composite for one set of pumps complete with Main Incoming MCB, individual pump VFDs and MPCB with single phasing preventer, contactors, control contactors, dry run trip relay with presure/flow transmitter in suction header, ON-OFF and TRIP Indicating LED type lamps, PLC based pump controller suitable to work as per operation logic furnished, cascade operation, automatic working/standby selection for equal run time ,cyclic timer etc. suitable for the pump capacity as specified below. Panel shall have auto-manual - off switch for operation in manual mode/automation mode. Panel to have necessary provisions of control relays to provide potential free contacts for BMS controls and monitoring.
Set of accessories such as G.I headers for suction and discharge, control valves, non return valves, pressure/flow transducers in suction and discharge lines (both), pressure gauge, electronic flow /level switch with cables for dry run protection and complete inter connecting power and control cabling and all required instumentation complete shall be included in the offer. Hydro booster pressure vessel of approx. 100 liters capacity rated for 20 bar pressure with interchangeable butyl rubber membrane shall be mounted on the system. Vendor to confirm the capacity of tank and pressure rating
1.2 |  | Domestic Water Transfer Pumps [ From UGT to OHT]
|  | Supplying, installing, testing and commissioning pressur booster pump. Flow Capacity: 12m3/hr each pump 50 mtr head with 100 Ltr Tank Location - Pump Room 1 Set = (1 Working + 1 Standby - cascade operation) Suction head - positive suction Make - Lubi, Xylem | 1 | Set
2 |  | PUDDLE FLANGES
a |  | 65mm dia | 2 | Nos
3 |  | Providing and fixing in position the PVC coated steps of size 300x150mm for tanks including placing 150mm inside concrete (while doing form work), aligning during concreting, grouting the junction if required, cleaning etc., | 26 | Nos
4 |  | Providing and fixing CI / FRPmanhole cover with frame for water storage tanks, medium duty (60kgs), water tight with seal of circular / rectangular dimensions, with lifting and locking arrangements as per approved sample including carting to site of work, fixing in C.C (1:2:4) and finishing with 3 coats of anti-corrosive paint, etc. complete as directed by E-I-C , Make: Thermodrain / Strong drain
a) |  | 600 dia | 4 | nos
Total of Schedule - A3
Total of Schedule - A1 to A3